## Introduction
PELLETS@LAS Wood Pellet Boiler Calculation Tool
Introduction
User instruction
1. Read instructions carefully - this sheet
2. Input data in the "Input" sheet cells marked green. Information in the "Input assistance" sheet can be used.
3. View the results of the calculation in the "Results" sheet
What does the tool do and how can it be used
The PELLETS@LAS Wood Pellet Boiler Calculation Tool provides a free estimate of the nominal wood pellet boiler
size and potential fuel cost savings when substituting an oil fired or natural gas fired boiler with a wood pellet
boiler at the current fuel price level. The tool is designed to handle boiler systems for small and medium sized
residential buildings and is fully open for the user to see, understand and alterate.
The calculation is based on user input regarding actual fuel consumption, fuel prices, geographical situation
etc. that is available from the PELLETS@LAS website and other websites. Calculation of the nominal boiler
capacity is based on a duration curve that shows the annual hourly heat demand of the house organised by size.
The curve shows the constant heat demand (hot water) and the variable demand (space heating), the area below
the curve being the existing heat demand of the house. The constant demand is calculated as a linear function of
the number of inhabitants while the variable demand is based on hardiness zone (design temperature) and degree
day number for the specific country. One degree day is an expression of a difference of one degree between the
inside (17 °C) and outside mean daily temperature.
The pellet boiler layout can be chosen by the user: Either the pellet boiler is layed out to cover the peak heat load
of the house on the coldest day or the pellet boiler is chosen to cover only a part of this peak while a fossil fuel
boiler is maintained for spare and peak load conditions. In any case the pellet boiler will cover the majority of the
heat demand. Choosing the latter solution will give the best technical and economical performance of a pellet boiler.
However, it is necessary to have more boiler room space and to keep the fossil fueled boiler stand by.
The annual fuel cost reduction is calculated as the difference between the existing fuel costs and the cost of the
wood pellets needed to generate the same amount of heat.
Limitations
The PELLETS@LAS Wood Pellet Boiler Calculation Tool provides a mere initial estimate for the boiler size and
wood pellet consumption. The tool cannot be used for design of a boiler plant. The calculation is based on user
input and may be influenced by national, regional or local variations. The full responsibility for the use of the
tool lies with the user. Neither FORCE Technology nor the PELLETS@LAS project consortium accepts any
liability for the use or the results of the use of the tool.
The sole responsibility for the content of this web site lies with the authors. It does not necessarily reflect opinion of the European
Communities. The European Commission is not responsible for any use that may be made of the information contained therein.
Boiler capacity
Hours

## Input
PELLETS@LAS Wood Pellet Boiler Calculation Tool
Input
Please work yourself through all the variables below by choosing or typing in values. Help can be found in the
"Input assistance" sheet and results of the calculation can be found in the "Results" sheet.
Climate conditions
Country | Greece
Climate zone | 10
Existing heat supply
Existing boiler age | Newer boiler (condensing)
Existing heating fuel | Heating oil
Existing average annual fuel consumption | 2000 | litres
Existing fuel price | 1.4 | €/litre | including taxes and VAT
Household details
Number of inhabitants | 4
Wood pellet price and boiler layout
Wood pellet price | 300 | €/tonne | including taxes and VAT
Pellet boiler layout | The new pellet boiler covers the full heat demand
The sole responsibility for the content of this web site lies with the authors. It does not necessarily reflect opinion of the European
Communities. The European Commission is not responsible for any use that may be made of the information contained therein.
Note on C17: Please type in your existing average annual fuel consumption
Note on C18: Please type in your existing fuel price (using the unit indicated)
Note on C22: Please fill in the number of persons in the house concerned
Note on C26: Please fill in he expected wood pellet price incl. taxes and VAT.

## Input assistance
PELLETS@LAS Wood Pellet Boiler Calculation Tool
Input assistance
This sheet contains information for the input sheet as well as data used for the calculations.
Boiler condition
Existing boiler contition | Age | Annual efficiency
Newer boiler (condensing) | <10 years | 1
Medium aged boiler | 10-20 years | 0.85
Old boiler | >20 years | 0.7
Fossil fuel
Fossil Fuel options | Amount unit | Heating value |  | Price unit
Heating oil | litres | 10 | kWh/litre | €/litre
Natural gas | Nm³ | 11 | kWh/Nm³ | €/Nm³
Climate conditions
The climate zone for your location can be found by using the hardiness zone map in this link:
http://www.gardenweb.com/zones/europe/
Climate zone (used for calculation) | Zone no. | Low average min. temp. (°C) | Av. min. temp. (°C)
| 3 | -40 | -40 / -35
| 4 | -35 | -35 / -29
| 5 | -29 | -29 / -23
| 6 | -23 | -23 / -18
| 7 | -18 | -18 / -12
| 8 | -12 | -12 / -7
| 9 | -7 | -7 / -1
| 10 | -1 | -1 / 5
Country info
Country | Degree days | Natural gas heating value
(MJ/Nm³)
Austria | 3395 | 38
Belgium | 2666 | 31
Bulgaria | 2000 | 38
Cyprus | 707 | 39.5
Czech Republic | 3368 | 38
Denmark | 3239 | 39.5
Estonia | 4250 | 38
Finland | 5571 | 38
France | 2331 | 39.5
Germany | 3043 | 38
Greece | 1585 | 39.5
Hungary | 2779 | 38
Ireland | 2758 | 38
Italy | 1919 | 39.5
Latvia | 4081 | 38
Lithuania | 3892 | 38
Luxembourg | 2961 | 38
Malta | 470 | 39.5
Netherlands | 2672 | 31
Norway | 4200 | 39.5
Poland | 3428 | 38
Portugal | 1269 | 39.5
Romania | 2700 | 38
Slovakia | 3289 | 38
Slovenia | 2836 | 38
Spain | 1776 | 39.5
Sweden | 5200 | 39.5
Switzerland | 3000 | 38
United Kingdom | 3183 | 38
Degree days source: http://www.swivel.com/data_sets/show/1006352
The natural gas heating values are estimates based on interviews with Danish and international expert bodies
and may be changed if better ones are available.
Fossil fuel price
The fuel price can be found on your energy bill, by contacting the supplier or by checking supplier websites.
Wood pellet price
Please find your pellet price by contacting a local pellet supplier or searching the Internet. PELLETS@LAS
provides price information as well as contact data for suppliers. |  | www.pelletsatlas.info
Wood pellet data and pellet boiler layout
Annual boiler efficiency | 0.85
Wood pellet heating value | 4900 | kWh/tonne
Layout of the new pellet boiler | Sizing factor | Heat demand coverage
A fossil fuel boiler covers spare and peak load | 0.75 | 0.95
The new pellet boiler covers the full heat demand | 1.2 | 1
Please feel free to alter the efficiency or heating value after consulting your suppliers.
Household details
The number of inhabitants indicates the hot water consumption which equals the share of the heat
consumption that is independent of climatic variations.
The default daily heat demand for hot water: | 4 | kWh/person
The sole responsibility for the content of this web site lies with the authors. It does not necessarily reflect opinion of the European
Communities. The European Commission is not responsible for any use that may be made of the information contained therein.
Note on D18: Retreived from the country info below
Note on C41: Estimated value
Note on C58: Estimated value
Note on C61: Estimated value
Note on C66: Estimated value

## Results
PELLETS@LAS Wood Pellet Boiler Calculation Tool
Results
Nominal Boiler Capacity
Based on your input, the optimal nominal pellet boiler capacity is estimated to:
| 8.8 | kW
With this size boiler, wood pellets cover the majority of the annual heat demand.
Please refer to the PELLETS@LAS wood pellet handbooks for more information on boiler design.
Annual wood pellet consumption and savings
Based on your input, substituting the majority or all of the fossil fuel with wood pellets will save you around:
| 1400 | €/year
This amount reflects only the fuel cost savings. Other costs such as electricity, service and maintenance may
influence the picture. Please refer to the PELLETS@LAS wood pellet handbooks for more information on boiler
operation. And please refer to the boiler supplier for more information on electricity consumption.
Basis for the estimate
The following input data and calculated values have been used for calculating the above results:
Climate conditions
Country | Greece
Climate zone | 10
Existing heat supply
Existing boiler age | Newer boiler (condensing)
Existing heating fuel | Heating oil
Existing average annual fuel consumption | 2000 | litres
Existing fuel heaing value | 10 | kWh/litre
Existing fuel price | 1.4 | €/litre
Existing annual heat demand | 20000 | kWh
Household details
Number of inhabitants | 4
Wood pellet price and boiler layout
Wood pellet price | 300 | €/tonne
Pellet boiler layout | The new pellet boiler covers the full heat demand
The sole responsibility for the content of this web site lies with the authors. It does not necessarily reflect opinion of the European
Communities. The European Commission is not responsible for any use that may be made of the information contained therein.
Note on D38: Calculated